## Sheet1
Name | Measures | Energy Use Intensity | Peak Electric Demand | Electricity Consumption | Natural Gas Consumption
|  | (kBtu/ft2-yr) | (kW) | (kWh) | (Million Btu)
|  | 39.4 | 12.9 | 42403.3 | 71.8
Name | Measures | Energy Use Intensity Reduction | Peak Electric Demand Reduction | Electricity Savings | Natural Gas Savings
|  | (kBtu/ft2-yr) | (kW) | (kWh) | (Million Btu)
Baseline |  | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%
Alternative 26 | Option 1 Name | 8.7 | 1.5 | 1,603.3 | 42.6
|  | 22% | 12% | 4% | 59%
Alternative 25 | Option 1 Name | -1.9 | 0.0 | -31.9 | -10.4
|  | -5% | 0% | 0% | -14%
Alternative 24 | Option 1 Name | 0.0 | 0.0 | -71.9 | 0.0
|  | 0% | 0% | 0% | 0%
Alternative 23 | Option 1 Name | 0.0 | 0.1 | 35.7 | 0.0
|  | 0% | 1% | 0% | 0%
Alternative 22 | Option 1 Name | 0.0 | 0.0 | -1.9 | 0.0
|  | 0% | 0% | 0% | 0%
Alternative 21 | Option 1 Name | 0.0 | 0.0 | 0.3 | 0.0
|  | 0% | 0% | 0% | 0%
Alternative 20 | Option 1 Name | -0.1 | 0.0 | -84.8 | 0.0
|  | 0% | 0% | 0% | 0%
Alternative 19 | Option 1 Name | -0.1 | -0.1 | -129.2 | 0.0
|  | 0% | -1% | 0% | 0%
Alternative 18 | Option 1 Name | -1.3 | 0.1 | -22.7 | -7.2
|  | -3% | 0% | 0% | -10%
Alternative 17 | Option 1 Name | -1.3 | 0.1 | -19.7 | -7.2
|  | -3% | 0% | 0% | -10%
Alternative 16 | Option 1 Name | -1.3 | 0.1 | -27.8 | -7.2
|  | -3% | 1% | 0% | -10%
Alternative 15 | Option 1 Name | -1.3 | 0.1 | -19.7 | -7.2
|  | -3% | 0% | 0% | -10%
Alternative 14 | Option 1 Name | -0.6 | 0.0 | -6.0 | -3.6
|  | -2% | 0% | 0% | -5%
Alternative 13 | Option 1 Name | -0.3 | -0.3 | -653.9 | 0.6
|  | -1% | -2% | -2% | 1%
Alternative 12 | Option 1 Name | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%
Alternative 11 | Option 1 Name | -0.4 | -0.3 | -509.4 | -0.3
|  | -1% | -2% | -1% | 0%
Alternative 10 | Option 1 Name | -4.3 | 0.1 | -9,473.0 | 8.7
|  | -11% | 1% | -22% | 12%
Alternative 9 | Option 1 Name | 0.8 | 0.1 | 1,474.3 | -0.6
|  | 2% | 1% | 3% | -1%
Alternative 8 | Option 1 Name | 0.7 | 0.0 | 1,379.3 | -0.8
|  | 2% | 0% | 3% | -1%
Alternative 7 | Option 1 Name | -10.4 | 0.1 | -3,546.6 | -45.3
|  | -27% | 1% | -8% | -63%
Alternative 6 | Option 1 Name | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%
Alternative 5 | Option 1 Name | -4.4 | 0.1 | -4,718.2 | -8.2
|  | -11% | 1% | -11% | -11%
Alternative 4 | Option 1 Name | -4.3 | 0.0 | -4,842.5 | -7.1
|  | -11% | 0% | -11% | -10%
Alternative 3 | Option 1 Name | 0.0 | 0.1 | 77.4 | -0.4
|  | 0% | 1% | 0% | -1%
Alternative 2 | Option 1 Name | -0.8 | 0.0 | -347.2 | -3.2
|  | -2% | 0% | -1% | -4%
Alternative 1 | Option 1 Name | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%

## Sheet2
Name | Measures | Energy Use Intensity | Peak Electric Demand | Electricity Consumption | Natural Gas Consumption
|  | (kBtu/ft2-yr) | (kW) | (kWh) | (Million Btu)
|  | 39.4 | 12.9 | 42403.3 | 71.8
Name | Measures | Energy Use Intensity Reduction | Peak Electric Demand Reduction | Electricity Savings | Natural Gas Savings
|  | (kBtu/ft2-yr) | (kW) | (kWh) | (Million Btu)
Baseline_NoFault |  | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%
SupplyAirLeakage | Option 1 Name | 8.7 | 1.5 | 1,603.3 | 42.6
|  | 22% | 12% | 4% | 59%
ReturnAirLeakage | Option 1 Name | -1.9 | 0.0 | -31.9 | -10.4
|  | -5% | 0% | 0% | -14%
PresenceOfNoncondensable | Option 1 Name | 0.0 | 0.0 | -71.9 | 0.0
|  | 0% | 0% | 0% | 0%
NonstandardCharging | Option 1 Name | 0.0 | 0.1 | 35.7 | 0.0
|  | 0% | 1% | 0% | 0%
LiquidLineRestriction | Option 1 Name | 0.0 | 0.0 | -1.9 | 0.0
|  | 0% | 0% | 0% | 0%
EvaporatorFouling | Option 1 Name | 0.0 | 0.0 | 0.3 | 0.0
|  | 0% | 0% | 0% | 0%
CondenserFouling | Option 1 Name | -0.1 | 0.0 | -84.8 | 0.0
|  | 0% | 0% | 0% | 0%
CondenserFanDegradation | Option 1 Name | -0.1 | -0.1 | -129.2 | 0.0
|  | 0% | -1% | 0% | 0%
BiasedEconomizerSensor_RAT | Option 1 Name | -1.3 | 0.1 | -22.7 | -7.2
|  | -3% | 0% | 0% | -10%
BiasedEconomizerSensor_RARH | Option 1 Name | -1.3 | 0.1 | -19.7 | -7.2
|  | -3% | 0% | 0% | -10%
BiasedEconomizerSensor_OAT | Option 1 Name | -1.3 | 0.1 | -27.8 | -7.2
|  | -3% | 1% | 0% | -10%
BiasedEconomizerSensor_OARH | Option 1 Name | -1.3 | 0.1 | -19.7 | -7.2
|  | -3% | 0% | 0% | -10%
BiasedEconomizerSensor_MAT | Option 1 Name | -0.6 | 0.0 | -6.0 | -3.6
|  | -2% | 0% | 0% | -5%
AHUFanDegradation | Option 1 Name | -0.3 | -0.3 | -653.9 | 0.6
|  | -1% | -2% | -2% | 1%
ThermostatBias | Option 1 Name | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%
OversizedEquipment | Option 1 Name | -0.4 | -0.3 | -509.4 | -0.3
|  | -1% | -2% | -1% | 0%
LightingSetback_NoSetback | Option 1 Name | -4.3 | 0.1 | -9,473.0 | 8.7
|  | -11% | 1% | -22% | 12%
LightingSetback_EarlyTermination | Option 1 Name | 0.8 | 0.1 | 1,474.3 | -0.6
|  | 2% | 1% | 3% | -1%
LightingSetback_DelayedOnset | Option 1 Name | 0.7 | 0.0 | 1,379.3 | -0.8
|  | 2% | 0% | 3% | -1%
HVACSetback_NoSetback | Option 1 Name | -10.4 | 0.1 | -3,546.6 | -45.3
|  | -27% | 1% | -8% | -63%
ImproperTimeDelaySettingInOccSensor | Option 1 Name | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%
HVACSetback_EarlyTermination | Option 1 Name | -4.4 | 0.1 | -4,718.2 | -8.2
|  | -11% | 1% | -11% | -11%
HVACSetback_DelayedOnset | Option 1 Name | -4.3 | 0.0 | -4,842.5 | -7.1
|  | -11% | 0% | -11% | -10%
ExcessiveInfiltration | Option 1 Name | 0.0 | 0.1 | 77.4 | -0.4
|  | 0% | 1% | 0% | -1%
EconomizerDamperStuck | Option 1 Name | -0.8 | 0.0 | -347.2 | -3.2
|  | -2% | 0% | -1% | -4%
DuctFouling | Option 1 Name | 0.0 | 0.0 | 0.0 | 0.0
|  | 0% | 0% | 0% | 0%